## BOARD OF TECHNICAL EDUCATION

PORVORIM-GOA

April, 2018 Examinations

Programme: Electrical Engg.

Subject: Distribution & Estimation(4108)/(EE511) [Old/Rev]

# Time Duration: 3 Hrs.                                               Max. Marks:  75

Instructions: 1) All Questions are compulsory.

2) Figures to the right indicate full marks.

3) Assume suitable additional data if required.

| Q.No.1. | Answer any five of the following Questions: | 5 x 3 = 15 |
| --- | --- | --- |
| a) | Compare single phase 2 wire ac system with 3 phase 4 wire system. |  |
| b) | A single phase has two parallel conductors 2m apart. The diameter of each conductor is 1.2cm. Calculate the loop inductance per Km of the line. |  |
| c) | What are the main requirements of line supports? |  |
| d) | With the help of neat diagram, explain Godown wiring. |  |
| e) | Compare ring and interconnected distribution system with reference to (i) Initial cost (ii) Supply reliability (iii) Maintenance cost. |  |
| f) | State the factors to be considered while selecting the size of conductors for AC distributors. |  |
| g) | State any three advantages of SWER system. |  |
| Q.No.2. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | With the help of a neat sketch explain radial distribution system. State its advantages and disadvantages. |  |
| b) | A single phase AC distributor 1 Km long supplies a load of 100A at 0.8 p.f. lagging at its far end and a load of 50A at 0.6 p.f. lagging at its mid point. The resistance and reactance per conductor per Km are 0.025 and 0.05 ohms respectively. Calculate the voltage at i) midpoint ii) sending end, if the receiving end voltage is 200V. |  |
| c) | Explain the method of solving ac distribution problems when the power factor of the load currents are referred with respect to receiving end voltage. Also draw phasor diagram of AC distributor. |  |
| Q.No.3. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | What is the role of insulator in distribution system? List out any five advantages of suspension type insulator over pin type insulator. |  |
| b) | Explain why earthing of distribution line is done? Explain with sketch the arrangement of earthing of line. |  |
| c) | 1 Km long CT overhead distribution line 3 phase 4 wire, 50 HZ is to be erected from a 125KVA mounted substation. RCC poles of 7.5m is to be used. Make a list of material required, if the span between adjacent is 50m. 6/1 x 2.59 mm ACSR conductor is to be used for 3 phase wires & 6/1 x 2.11 mm is to be used for neutral wires. |  |
| Q.No.4. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Explain ABC system for rural electrification. State its advantages and disadvantages. |  |
| b) | State important I.E. rules for domestic wiring. |  |
| c) | Draw and explain circuit diagram of: i) Three lamps & one socket outlet controlled by individual switches ii) Staircase wiring. |  |
|  | -2- | …….2/- |
| Q.No.5. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Name the various types of wiring system. Compare them on the basis of cost, life, maintenance, appearance, protection against mechanical injury, fire & moisture. |  |
| b) | Explain bus way system (overhead) of industrial wiring. List out its advantages & disadvantages. |  |
| c) | In a workshop, one 20 HP 415V, 50HZ three phase induction motor is to be installed. - Draw a single line diagram of the motor. - Find the full load current of the motor. - Find the size of the cable to be used. - Find the rating of the switch fuse. Given efficiency of the motor is 0.8 and power factor is 0.85. |  |
| Q.No.6. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | State important points to be considered while executing industrial wiring. |  |
| b) | With the help of neat diagram, explain plate earthing. |  |
| c) | (i)What is double earthing? What are its advantages? | (3) |
|  | (ii) Explain in brief, the various methods of improving earth resistance. | (3) |

***********