## BOARD OF TECHNICAL EDUCATION

PORVORIM-GOA

November, 2016 Examinations

Programme: Fabrication Technology & Erection Engg.

Subject: Piping Fabrication & Installation(5342) [Old]

# Time Duration: 3 Hrs.                                               Max. Marks:  75

Instructions: 1) All Questions are compulsory.

2) Figures to the right indicate full marks.

3) Assume suitable additional data if required.

4) Dimensions in the figures are in mm unless specified.

5) Refer to the data provided in the Question paper.

| Q.No.1. | Answer any five of the following Questions: | 5 x 3 = 15 |
| --- | --- | --- |
| a) | Consider an overhead tank of 10000L capacity for storage of water. Consider also that there are two sources of water supply: (From tank water goes to a cooling condenser on ground floor) - Public water supply - Water sump of 20,000L on ground floor pumping to overhead tank Using appropriate symbols, draw the process flow diagram for this process. |  |
| b) | What is the main effect of temperature on a pipe carrying hot fluid? How can it be overcome? |  |
| c) | What are the various ways in which a valve finds use in pipeline? (atleast 6 different purposes for its use) |  |
| d) | Illustrate how hot insulation is done on a generally used pipeline. Explain in brief. |  |
| e) | Name 3 different standards with initials and full title of organisation used in piping design and fabrication worldwide. |  |
| f) | In piping drawings, what is the importance of clearances and tolerances? Give examples. |  |
| g) | How can non-destructive testing be used in pipeline testing? |  |
| Q.No.2. | Design a pipe of material ASTM A106 G3-B to fabricate a pipeline to conduct fluid at 200C, pressure of 10Kg/cm2, velocity of flow=1.2 m/s, corrosion factor= 1.6mm for M.S., =0.4, E=0.85 and other details given in Table C for reference. The pipeline has total length of 100m, consisting of fittings of which relevant data is given in Table A & Table B, which are, 90 LR Elbow – 14, 90 SR Elbows – 10, Straight Tee – 3, Plug valve 1, check valve 2 and Gate valve 1. | (12) |
| Q.No.3. | Answer the following Questions: |  |
| a) | Draw the front view, top view, side view and developed view of the portion of pipeline whose Isometric view is shown in fig.1.(Drawing need not be to scale, but show dimensions clearly) | (8) |
| b) | Make a bill of materials of the pipeline shown in Fig.1, Q.3(a). | (4) |
| Q.No.4. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Convert the single line diagrams shown in fig.2 to double line orthographic drawing. Use suitable scale. |  |
| b) | Explain the water carrying pipe joints preparation of plastic pipes. | …..2/- |
| c) | What are the special points to be considered for the following types of pipelines: (Mention at least 3 points each) - Underground - Freeze protection of outdoor pipeline |  |
| Q.No.5. | Answer any three of the following Questions: | 3 x 4 = 12 |
| a) | Draw neat sketches of each of the following piping components: - Stanchion pipe support – 1 view - A Reducer - 1 view - Steam trap - 1 view - Flange with raised face - 2 views |  |
| b) | Assuming 4 floors of an Industrial shed and that pipes are running on all floors starting from ground floor, illustrate how heights and levels (altitudes) of pipelines are shown with dimensions in elevation view. |  |
| c) | Give specific features of any two non-metallic pipes. |  |
| d) | Enlist the factors influencing the decision of material of construction of a pipeline. |  |
| e) | Explain clearly what is shown and what is not shown in PFDs. |  |
| Q.No.6. | Write short notes on any three: | 3 x 4 = 12 |
| a) | Pre heating and post weld heat treatment |  |
| b) | Prefabrication planning of pipeline welding |  |
| c) | Material Inspection for pipeline fabrication |  |
| d) | Selection of welding process |  |
| e) | Weather protection of pipelines |  |