## BOARD OF TECHNICAL EDUCATION

PORVORIM-GOA

November, 2016 Examinations

Programme: Electrical Engg.

Subject: Testing & Maint. of Electrical Machines(EE613)/ Testing & Maint. of

Electrical Equip.(5104) [Old/Rev]

# Time Duration: 3 Hrs.                                               Max. Marks:  75

Instructions: 1) All Questions are compulsory.

2) Figures to the right indicate full marks.

3) Assume suitable additional data if required.

| Q.No.1. | Answer any five of the following Questions: | 5 x 3 = 15 |
| --- | --- | --- |
| a) | Sate three advantages & three disadvantages of direct method of testing Electrical machines. |  |
| b) | For a d.c. machine as a motor, define i) Mechanical efficiency ii) Electrical efficiency and iii) Overall efficiency. |  |
| c) | How phasing out test is performed on a 3-phase transformer? What is its significance? |  |
| d) | What would be the minimum insulation resistance between all windings together and frame of an induction motor rated as 100KW, 3.3 KV, 3-phase, 50Hz, 750rpm? Give rating of Megger to be used. |  |
| e) | Explain the power flow diagram of a 3 phase Induction motor. |  |
| f) | List down at least 6 type of tests to be performed on 3-phase induction motor. |  |
| g) | Give the classification of losses taking place in synchronous machine. |  |
| h) | Give four causes of failure of three phase induction motor. |  |
| Q.No.2. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | With neat diagram explain the procedure for determination of efficiency of a D.C. machine using the brake test. |  |
| b) | What are the advantages and disadvantages of testing d.c. machines by using Hopkinson test? |  |
| c) | With a neat circuit diagram, explain the Swinburne’s test on d.c. machine. How efficiency of d.c. machine is calculated from it? |  |
| Q.No.3. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | What are the two high voltage tests to be performed on transformer? Explain any one in detail. |  |
| b) | Enlist the various routine tests to be performed on a transformer. |  |
| c) | With neat diagram explain the O.C. and S.C. test to be performed on a transformer to determine its efficiency and losses. |  |
| Q.No.4. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | State and explain the methods of measurement of temperature rise of various parts of 3-phase induction motor. |  |
| b) | A 4-pole, 50Hz, 230V, 5HP, 3-phase induction motor gave the following test data: No load test; 275W; 6.3A; 230V. Blocked rotor test; 735W; 15A; 40V. Determine the efficiency of the motor at full load from the above data. | ……2/- |
|  | -2- |  |
| c) | State and explain the acceptance tests to be performed on 3-phase induction motor. Why these tests are necessary? |  |
| Q.No.5. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | i) Justify the statement – “Generally large capacity machines are tested by indirect method of testing”. ii) State difference between type tests and routine tests. | (3) (3) |
| b) | Explain how the efficiency of synchronous machine can be determines by using summation of losses method. |  |
| c) | With a neat diagram, explain the Sumpner’s test to be performed on single phase transformers. |  |
| Q.No.6. | Write short notes on any two: | 2 x 6 = 12 |
| a) | Maintenance schedule for power transformer |  |
| b) | Pre-commissioning tests on a 3-phase induction motor |  |
| c) | Care of Electrical equipment during period of inactivity and storage |  |

***********