## BOARD OF TECHNICAL EDUCATION

PORVORIM-GOA

April, 2012 Examinations

Programme: Electrical Engg.

Subject: Generation & Transmission(4114)

# Time Duration: 3 Hrs.                                               Max. Marks:  75

Instructions: 1) All Questions are compulsory.

2) Figures to the right indicate full marks.

3) Assume suitable additional data if required.

| Q.No.1. | Answer any five of the following Questions: | 5 x 3 = 15 |
| --- | --- | --- |
| a) | Define i) diversity factor (ii) load factor. |  |
| b) | State the location of surge tank in hydroelectric power plant? What is its function? |  |
| c) | Discuss the methods of starting stand-by diesel generator set. |  |
| d) | What do you understand by short, medium and long transmission lines? |  |
| e) | Why bundled conductors are used in overhead transmission lines? |  |
| f) | State the specification required for procurement of a pin insulator. |  |
| Q.No.2. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Draw the schematic diagram of a hydroelectric power generating station and state the function of its parts. |  |
| b) | A proposed station has the following daily load cycle. Time in Hrs; 6-8; 8-12; 12-16; 16-19; 19-24; 24-6. Load in MW; 30; 40; 60; 80; 40; 30. Draw the load curve and select suitable generator units. Prepare operation schedule for machine selected and load factor from the curve. |  |
| c) | What do you understand by grid system? Give merits and demerits of grid system. |  |
| Q.No.3. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | State and explain the type of speed governors used in Diesel generator set. |  |
| b) | Describe wind power generation with a neat diagram. |  |
| c) | Briefly explain what do you mean by base load and peak load. Compare base load and peak load power plants. |  |
| Q.No.4. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | A 3 phase overhead transmission line is being supported by three disc insulators. Potential across top unit and middle unit are 8 KV and11 KV respectively. - Calculate ratio of capacitance between pin and earth to the mutual capacitance of each unit. - Line voltage. - String efficiency. |  |
| b) | Explain in brief different support structures used in transmission lines. |  |
| c) | Write a short note on effect of variation of transmission voltage and load power factor on performance of short transmission lines. | ….2/- |

-2-

| Q.No.5. | Answer any two of the following Questions: | 2 x 6 = 12 |
| --- | --- | --- |
| a) | A 3 phase transmission line 200km long has the following constants. Resistance per Km = 0.15 Reactance per Km =0.50 Susceptance per Km = 2.0 x 10-6 mho Voltage at receiving end is 132 KV. The transmission line is delivering 50MVA at 0.85 p.f. lagging at the receiving end. Calculate i) Sending end voltage (ii) sending end current (iii) voltage regulation (iv) line efficiency using nominal  method . |  |
| b) | State the advantages and disadvantages of corona. |  |
| c) | Briefly give the classification of transmission lines. |  |
| Q.No.6. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Write a short note on vibration dampers. |  |
| b) | A transmission line has a span of 200m between level supports. The conductor has a cross sectional area of 1.29cm2 and weighs 1170 Kg/Km and has a breaking stress of 4218 kg/cm. Calculate the sag for a safety factor of 5, allowing a wind pressure of 122 Kg per square meter of projected area. Calculate the vertical sag. |  |
| c) | What is a Sag template? Explain how this is useful for location of towers and stringing of conductors. |  |

***********