## BOARD OF TECHNICAL EDUCATION

PORVORIM-GOA

April, 2015 Examinations

Programme: Mechanical Engg.

Subject: Principles of Airconditioning(5047)

# Time Duration: 3 Hrs.                                           Max. Marks: 75

Instructions: 1) All Questions are compulsory.

2) Figures to the right indicate full marks.

3) Assume suitable additional data if required.

4) Use of Psychrometric charts is permissible.

| Q.No.1. | Answer any five of the following Questions: | 5 x 3 = 15 |
| --- | --- | --- |
| a) | Define following psychrometric properties of air: i) Relative humidity ii) Wet bulb temperature iii) Dew point temperature. |  |
| b) | Draw a Psychrometric chart and show relative humidity lines, specific volume lines & constant enthalpy lines on it. |  |
| c) | Define: i) Throw ii) Drop in air distribution system. |  |
| d) | Show on psychrometric chart following air conditioning processes: i) Cooling and humidifying ii) Heating and dehumidifying. |  |
| e) | What is ‘Economic insulation thickness’? |  |
| f) | What is infiltration air load? What are the sources of infiltrated air? |  |
| g) | What are the basic elements of air conditioning control systems? |  |
| Q.No.2. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | 200 m3 of air per minute is passed through the adiabatic humidifier. The condition of air at inlet is 40C DBT and 15% RH and the outlet condition is 25C DBT and 20C WBT. Find i) Dew point temperature ii) Amount of water vapour added to the air per minute. |  |
| b) | State Dalton’s law of partial pressure. Also with neat sketch explain ‘sling psychrometer’. |  |
| c) | 39.6 m3/min of a mixture of recirculated room air and outdoor air enter a cooling coil at 31C DBT & 18.5C WBT. The effective surface temperature of the coil is 4.4 C. The surface area of the coil is such as would give 12.5 KW of refrigeration with the given entering air state. Determine the dry and wet bulb temperatures of the air leaving the coil and the coil by–pass factor. |  |
| Q.No.3. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | An air conditioning system is designed under the following condition: Outdoor condition = 30C DBT, 75 % RH Required indoor conditions = 22C DBT, 70% RH Amount of free air circulated = 3.33 m3/s Coil dew point temperature = 14C The required condition is achieved first by cooling and dehumidifying, and then by heating. Determine: i) capacity of the cooling coil in TR ii) capacity of the heating coil in KW iii) Amount of water vapours in Kg/s. |  |
| b) | Enumerate and explain the components of internal heat gains. | …….2/- |
|  | -2- |  |
| c) | The following data relate to a conference room for seating 100 persons. Inside design conditions = 22C DBT, 60% RH Outside design conditions = 40C DBT, 27C WBT Sensible and Latent heat load per person = 80 W and 50 W Light and fan loads = 15000 W Air infiltration = 20 m3/min Sensible heat gain through glass, walls, ceiling, etc. = 15000 W. Fresh air supply = 100 m3/min. By-pass factor of the coils = 0.1 If two-third of recirculated room air and one –third of fresh air are mixed before entering the cooling coils, determine: i) Apparatus dew point ii) Grand total heat load iii) Effective room sensible heat factor. |  |
| Q.No.4. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Explain with neat diagram the working of central system of air-conditioning. |  |
| b) | Define a ‘Unitary system’. Where is it commonly preferred? Explain a room air-conditioner with neat sketch. |  |
| c) | Discuss briefly the various factors that are considered for air conditioning of: i) Hospital ii) Hotel. |  |
| Q.No.5. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | What is the function of a filter? How are filters classified? Explain briefly a self cleaning filter? |  |
| b) | Explain with neat sketches: i) Steam injection type humidifier ii) Spray type humidifier. |  |
| c) | What purposes is served by a fan? How are fans classified? |  |
| Q.No.6. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Explain ‘static regain method’ of duct design for air conditioning. Under what situation is this recommended? What are its main disadvantages? |  |
| b) | Explain with neat sketch “Two position electrical control system” used in air – conditioning. |  |
| c) | Explain in brief following control devices: i) Automatic humidity control ii) Air movement control. |  |

***********