## BOARD OF TECHNICAL EDUCATION

PORVORIM-GOA

April, 2015 Examinations

Programme: Electrical Engg./E&EE

Subject: Transformers(4106) [Old]

# Time Duration: 3 Hrs.                                           Max. Marks: 75

Instructions: 1) All Questions are compulsory.

2) Figures to the right indicate full marks.

3) Assume suitable additional data if required.

| Q.No.1. | Answer any five of the following Questions: | 5 x 3 = 15 |
| --- | --- | --- |
| a) | Define: Transformer. Why it has very high efficiency? |  |
| b) | With a neat diagram explain shell type transformer. |  |
| c) | Calculate rated primary and secondary current of a 100KVA, 11KV/415 volt, 3-phase transformer. |  |
| d) | What do you mean by leakage flux? How its effect is represented in equivalent circuit of a transformer? |  |
| e) | State any three applications of autotransformer. |  |
| f) | Briefly explain importance of Polarity check while connecting two transformers in parallel. |  |
| g) | List any three special features of Furnace transformer. |  |
| Q.No.2. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Briefly explain importance of following transformer components: i) Conservator ii) Explosion Vent. |  |
| b) | With a neat diagram explain working of On load tap changer. |  |
| c) | With a neat diagram explain helical winding. State its application. |  |
| Q.No.3. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Draw and explain phasor diagram of single phase transformer supplying R-L load. |  |
| b) | A single phase transformer has 1000 turns on primary and 200 turns on secondary. The no load current is 3.0 Amp at a p.f. of 0.2 lagging. Calculate the primary current and p.f. when secondary current is 280 Ampere at a p.f. of 0.8 lagging. |  |
| c) | A single-phase transformer has 180 and 90 turns respectively on its secondary and primary winding. The respective resistances are 0.233 ohm & 0.067 ohm. Calculate i) Equivalent resistance of primary referred to secondary ii) Equivalent resistance of secondary referred to primary iii) Total resistance referred to primary. |  |
| Q.No.4. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Define and explain importance of following w.r.t. Transformer i) Efficiency ii) Voltage Regulation. |  |
| b) | The primary of transformer is rated 10A and 1000V. On open circuit test the readings are V1=1000V, V2=500V, I1=0.42 A and W=100 watts. On short circuit test the readings are I1=10Amp, V1=126V, W=400 watts. Determine the parameters of equivalent circuit and draw equivalent circuit. |  |
| c) | A 100KVA transformer has 300 turns on primary and 60 turns on secondary. If the supply voltage is 2200V and R1=0.4, R2=0.01, X1=1.0 and X2=0.03, calculate: - % Voltage Regulation at full load and 0.8 p.f. lagging - % Voltage Regulation at Half full load and 0.8 p.f. leading. | …….2/- |
|  | -2- |  |
| Q.No.5. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Write a short note on effect of failure of cooling system on the performance of transformer. |  |
| b) | A 20 KVA, 11KV/440V transformer has iron loss of 1.5KW and full load copper loss of 2.0 KW. Determine the efficiency of transformer at i) 75% of full load ii) 50% of full load. |  |
| c) | A 100 KVA distribution transformer supplying load has full load copper loss and iron loss of 1.5 KW and 2.0 KW respectively. During a day (24 hours) the transformer is loaded as follows: 6 am to 12 am – half load 12 am to 6 pm – ¼ Full load 6 pm to 10 pm – Full load 10 pm to 6 am – negligible load Calculate All day efficiency of transformer. |  |
| Q.No.6. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Write a short note on checks before connecting two transformers in parallel. |  |
| b) | A load of 800KW at 0.8 p.f. lagging is supplied by two, 3-phase transformers rated 400 KVA and 600 KVA in parallel. Both transformers have same turns ratio and their p.u. resistances and reactances are given below: - 400 KVA transformer Rpu=0.02; Xpu=0.04 - 600 KVA transformer Rpu=0.01; Xpu=0.05 Calculate the load shared by each transformer and its power factor. |  |
| c) | Write a short note on welding transformer and its features. |  |

***********