## BOARD OF TECHNICAL EDUCATION

PORVORIM-GOA

November, 2013 Examinations

Programme: Electrical Engg.

Subject: Testing & Maintenance of Electrical Equipments(5104)

# Time Duration: 3 Hrs.                                               Max. Marks:  75

Instructions: 1) All Questions are compulsory.

2) Figures to the right indicate full marks.

3) Assume suitable additional data if required.

| Q.No.1. | Answer any five of the following Questions: | 5 x 3 = 15 |
| --- | --- | --- |
| a) | What is meant by Type Tests of an electrical equipment? State any four of them. |  |
| b) | Enlist the methods of measurement of winding resistance of a transformer. |  |
| c) | Explain the significance of open circuit and short circuit test on a power transformer. |  |
| d) | List any six routine tests to be conducted on an induction motor. |  |
| e) | State and classify the different losses taking place during operation of an induction motor. |  |
| f) | What is the necessity for conducting pre-commissioning tests? List any four of them for a power transformer. |  |
| g) | Explain the necessity for conducting sustained 3 short circuit test on a 3 synchronous machine. |  |
| Q.No.2. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | With a neat diagram explain the experimental set up and method for determination of efficiency of a DC machine using Brake test. |  |
| b) | A DC shunt machine while running as a motor on no-load draws 440 W at 220 V runs at 1000rpm. The field current is 1A and armature resistance is 0.5. Calculate the efficiency of this machine under following conditions: - When running as a generator delivering 40A at 220V. - When running as a motor and drawing 40A at 220V. Draw suitable figure. |  |
| c) | Two similar DC machines each rated at 500V, 1000W were tested by Hopkinson’s test. The data obtained was as follows: Generator output current = 2000A Input current from supply mains = 380A Shunt field current of generator = 22A Shunt field current of motor = 17A Resistance of armature circuit of each machine = 0.01 Calculate the efficiency of the generator at full load assuming equal iron, frictional and windage losses. Draw suitable figure. |  |
| Q.No.3. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | With a neat diagram explain in detail conduction of Sumpner’s test for determining the efficiency of 1 transformers. State any two advantages of this test. |  |

………2/-

-2-

| b) | A 50KVA single phase transformer draws primary current of 250A at full load. Total resistance referred to the primary side is 0.006. Considering iron loss of the transformer to be 200W, calculate the efficiency of the transformer at full load and efficiency of the transformer at full load and half full load with 0.8 power factor lagging. |  |
| --- | --- | --- |
| c) | State the various methods that can be adopted for temperature rise test on a power transformer. With neat diagram explain the / connection method. |  |
| Q.No.4. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | A 415V, 3, 50HZ, 6 pole, 0.8 p.f, Y connected Induction motor has following data: No load input power = 250W, No load current = 3.5A, Stator resistance per phase = 1.5, Full load current = 9.6A, Slip speed (Ns – Nr) = 40rpm, Total motor input power = 6KW. Find the efficiency of the motor by summation of losses. |  |
| b) | With a neat diagram explain the blocked rotor test on a 3 induction motor. Also plot the effect of variation of supply voltage over input power and stator current. |  |
| c) | The input power to a 500V, 50HZ, 6 pole, 3, induction motor running at 975 rpm is 40KW. The stator losses are 1KW and friction & windage losses total 2KW. Calculate: i) Slip ii) rotor copper loss iii) Output power in HP iv) the efficiency. |  |
| Q.No.5. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Explain the typical maintenance schedule to be followed for maintenance of a 3 slip ring induction motor as per IS. |  |
| b) | Explain the steps and care to be taken during storage of an electrical machine at the site. (Write atleast 8 points) |  |
| c) | Why and when does the revarnishing of windings of electrical equipments necessary? State the various methods of revarnishing. Briefly explain any one of them. |  |
| Q.No.6. | Write notes on any two: | 2 x 6 = 12 |
| a) | Impulse voltage with stand test on power transformer |  |
| b) | Sudden 3 short circuit test on synchronous machine |  |
| c) | Phatom loading method and its advantages |  |

***********